Table 4: Result of the sampling operations following the treatment of the water system, based on the type of disinfection treatment performed

|  | Sampling after treatment, n | Legionella isolated (%) | Legionella load > 103 CFU/L (%) | Legionella load > 104 CFU/L (%) |
| --- | --- | --- | --- | --- |
| Shock hyperchlorination (alone or combined) | 18 | 13 (72%) | 8 (44%) | 5 (28%) |
| Shock hyperchlorination alone | 10 | 7 (70%) | 6 (60%) | 4 (40%) |
| Heat shock (alone or combined) | 9 | 6 (67%) | 2 (22%) | 1 (11%) |
| Heat shock alone | 1 | 0 (0%) | 0 (0%) | 0 (0%) |
| Shock hyperchlorination plus heat shock | 7 | 5 (71%) | 1 (14%) | 1 (13%) |
| Shock hyperchlorination plus heat shock plus hydrogen peroxide (continuous) | 1 | 1 (100%) | 1 (100%) | 0 (0%) |